## Slide 1: Protection of Microgrids Using Differential Relays
Manjula Dewadasa
Arindam Ghosh
Gerard Ledwich
Notes: <number>

## Slide 2: Introduction – Protection Issues
A microgrid integrates distributed energy resources to provide reliable, environment friendly and economical power
A microgrid can operate either in grid-connected or islanded mode
Islanding operation brings benefits to customers
However, once islanding occurs, short circuit levels may drop significantly due to the absence of strong utility grid
In this case, protection system designed for high fault currents will not respond and new protection strategies are required to ensure a safe islanding operation in a microgrid

## Slide 3: Protection Issues Contd.
The power flow within a microgrid can be bi-directional due to
    DG connections at different locations
    mesh configuration
Most of DGs are connected through power electronic converters and these converters do not supply sufficient currents to operate current based protective devices
Some of the DGs connected to a microgrid are intermittent and therefore different fault current levels can be experienced
Protecting a converter dominated microgrid is a challenging technical issue

## Slide 4: Protection Solutions
Protection strategies required for a microgrid are presented using current deferential relays
The protection challenges associated with
    bi-directional power flow
    meshed configuration
    changing fault current level due to intermittent nature of DGs
    reduced fault current level in an islanded mode
are addressed
Notes: <number>

## Slide 5: Microgrid Configuration
Protection of the microgrid is discussed under different subgroups such as feeder, bus and DG
Link

## Slide 6: Differential Feeder Protection
Current differential protection is proposed to detect and isolate the feeder faults
The differential and bias currents are defined as
I1 and I2 are secondary CT phasor currents in each relay location

## Slide 7: Deferential Relay Characteristic
In normal operating condition, the differential current should be zero
However, due to the line charging, CT saturation and inaccuracies in CT mismatch, it may not equal to zero

## Slide 8: Deferential Bus Protection
Buses may have connected to loads, DGs and feeders
The relay will issue a trip command to all the circuit breakers connected to the bus during a bus fault

## Slide 9: CT Selection Criteria for Protection
IEEE C57.13 and IEEE C37.11provide guidelines in selecting CTs for protective relays
Following factors should be considered
  CT ratio
  CT accuracy class
  polarity
  saturation voltage
  knee point voltage
  excitation characteristic
  primary side voltage rating and current rating

## Slide 10: CT Selection Criteria Contd.
IEEE C57.13 and IEEE C37.11provide guidelines in selecting CTs for protective relays
Usually, the secondary rated current is 5A
The primary current rating of a CT is selected considering
  the maximum current in normal operating condition
  the maximum symmetrical fault current
The selected primary current should be greater than the maximum current in normal operating condition and it should also be greater than one twentieth (1/20) of the maximum symmetrical fault current

## Slide 11: CT Selection Criteria Contd.
The saturation due to both AC and DC components can be avoided by selecting the saturation voltage of a CT according to
Vx - secondary saturation voltage
IS - the ratio between the primary current and the CT turns ratio
RS - the CT secondary resistance
XL - the leakage reactance
ZB - the total secondary burden which includes secondary leads and devices
X - the primary system reactance
R - the resistance up to the fault point

## Slide 12: Microgrid Protection Studies
The CT ratio for a particular CT is selected based on the maximum load current and the maximum fault current seen by the relay.
The CT ratio for a relay is selected based on
  the CT can deliver 20 times rated secondary current without exceeding 10% ratio error
  the rated primary current to be above the maximum possible load current

## Slide 13: Simulation Results
The maximum CT ratio error of ±10% is assumed
Relay | Ifmax (A) | Ifmax/20 (A) | ILmax (A) | CT ratio
R12 | 2535 | 126 | 236 | 300:5
R21 | 1478 | 74 | 236 | 300:5
R15 | 2541 | 127 | 236 | 300:5
R51 | 956 | 48 | 236 | 300:5
R25 | 1111 | 56 | 184 | 200:5
R52 | 998 | 50 | 184 | 200:5
R23 | 1478 | 74 | 142 | 150:5
R32 | 917 | 46 | 142 | 150:5
R34 | 917 | 46 | 79 | 100:5
R43 | 654 | 33 | 79 | 100:5

## Slide 14: Simulation Results Contd.
The fault response of relays R23 and R32 for internal and external feeder faults
The fault resistance is varied from 1 Ω to 20 Ω

## Slide 15: Simulation Results Contd.
The fault response of relays R23 and R32 for internal and external feeder faults

## Slide 16: Relay Response in Islanded Operation
Relays R12 and R21 response for faults in islanded microgrid
Relays are capable of detecting faults either in grid connected or islanded modes of operation without changing any relay settings

## Slide 17: Conclusions
In this paper, a primary protection scheme for a microgrid is presented using current differential relays
The protection issues associated with meshed structure, microgrid islanded operation, fault detection under low fault current levels are avoided with the use of modern differential relays
Relay settings and CT selection requirements are also discussed
Results show that the proposed protection strategies can provide selectivity and high level of sensitivity for internal faults in both grid-connected and islanded modes of operation thereby allowing a safe and a reliable operation for a microgrid