## Slide 1: Protection of distributed generation connected networks with coordination of overcurrent relays
Manjula Dewadasa
Arindam Ghosh
Gerard Ledwich
Notes: <number>

## Slide 2: Introduction
Distributed generators (DGs) can provide benefits for both utilities and consumers
Power flow in a radial network become bi-directional once DGs are connected
The fault current level changes due to intermittent nature of DGs
The islanding operation with DGs is prohibited due to the restoration, personnel safety and power quality issues
However, the disconnection of DGs drastically reduces the benefits as the penetration level increases

## Slide 3: Introduction Contd.
According to IEEE Std. 1547, DGs should disconnect from the network when a fault occurs
The DGs can be used to supply the load demand in the absence of grid supply if DGs are allowed to operate in islanded mode.
In this paper, protection issues associated with disconnection of DGs are addressed in the context of a radial distribution feeder

## Slide 4: The major protection issues are identified as
Isolation of the smallest faulted section
Fault ride-through capability of DG and DG connection /disconnection
Islanded protection with DGs
System restoration by performing auto-reclosing
In this study, the abovementioned protection issues are addressed

## Slide 5: Isolation of the smallest faulted section
When a fault occurs in a traditional radial feeder, the overcurrent relays respond to isolate the portion of the network resulting power interruption to the customers downstream from the fault location
In the proposed method, customer power interruption is minimized by isolating the smallest faulted section from the network and allowing islanded operation
This is achieved by isolating a fault from both upstream and downstream sides

## Slide 6: Isolation of the smallest faulted section contd.
Directional overcurrent (OC) relays with separate grading in forward and reverse are proposed
If DG connections are not consistent, a reliable communication method is required amongst DGs and the relays
Then relays select the most appropriate setting according to present system configuration
In the case of communication failure, each relay selects its default settings which are initially defined

## Slide 7: Fault ride-through capability of DGs
The DGs should have the fault ride through capability to obtain faulted section isolation
This prevents unnecessary disconnections of DGs during abnormal conditions
In the proposed method, DGs inject fault current for a defined time period (td) until fault is cleared by the relays
The time td is chosen considering the relay requirements and DG disconnection requirements for abnormal voltages (IEEE 1547)

## Slide 8: Fault ride-through capability of DGs
If faulted section is isolated from the rest of system within the time td three types of DG status can be mainly identified
DGs connected to the utility grid
These DGs can operate in grid-connected mode after isolating the fault from the utility side
(2) DGs connected to the faulted section
DGs connected to the faulted section will be disconnected either using the DG circuit breaker
DGs connected to the islanded section
DGs can supply the load demand if the total DG capacity is sufficient to supply the load demand

## Slide 9: Islanded protection with DGs
The relays settings in forward direction will not be appropriate since they are initially set considering the utility fault current
Therefore, the relay settings are changed during the islanded operation
However, the DGs will be disconnected after the time period td thereby providing backup protection in the absence of relays or when the relays fail to detect a fault

## Slide 10: System restoration using auto-reclosing
A novel method for system restoration is proposed using automatic circuit reclosers (ACRs)
Directional OC relays are linked with the ACRs for system restoration
The restoration is started based on the identification of fault direction. A reclosing opportunity is given to the relay which sees the fault as forward.
For example, it is assumed that both forward and reverse relays are isolated the faulted section allowing an islanded operation beyond the downstream relay.

## Slide 11: System restoration using auto-reclosing
In this case, forward relay tries to close the ACR (live to dead reclosing) first after a pre-defined delay time period, tr that is greater than td
The time tr allows to disconnect any DG connected to the faulted section. This will also help in the self extinction of arc, if any
The downstream relay waits till upstream reclosing is successful. Only then it takes the opportunity to connect the downstream side with the upstream (utility) side

## Slide 12: Simulation studies
System Quantities | Values
System frequency | 50 Hz
Source voltage | 11 kV rms (L-L)
Source impedance (Zdg) | 0.39 + j 3.927 
Feeder impedance (Z12=Z23 =Z34) Positive sequence Zero sequence | 0.585 + j 2.9217 0.8775 + j 4.3825
Load power | 1.0 MVA, 0.8 pf
DG power rating | MVA
System parameters
The directional overcurrent relays R1, R2 and R3 are located at BUS-1, BUS-2 and BUS-3
DGs inject fault currents for a defined time period (td = 0.35 s) or until the fault isolation is achieved
If the fault is cleared within 0.35 s (i.e. defined time period), the converter will recover and start supplying power in either grid-connected or islanded mode

## Slide 13: Relay settings in forward direction
The relay grading is performed separately for forward and reverse directions
In forward direction, the relays are graded considering both utility and DG connections
The maximum and minimum fault current levels at each bus is calculated and used to set the inverse time and instantaneous relay elements.
In the reverse direction, relays can be only graded considering the DG fault currents

## Slide 14: Relay settings in forward direction contd.
Relay | CT ratio | Pickup current (A) | TMS
R1 | 250/5 | 5 | 0.15
R2 | 200/5 | 4.5 | 0.1
R3 | 200/5 | 4.5 | 0.05
Relay setting in forward direction
Relay tripping time characteristics in forward direction

## Slide 15: Relay settings in reverse direction
The maximum load current seen by each relay during normal operating condition is calculated
If an inverse time relay characteristic is selected, higher fault clearing time can be experienced since fault current is comparably small due to the current limiting of converters
Thus, definite time overcurrent relays are selected
Relay | CT ratio | Pickup current (A) | Time delay (s)
R2 | 200/5 | 5.9 | 0.1
R3 | 200/5 | 3.9 | 0.3
Definite time relay element settings in reverse direction

## Slide 16: Protection when DGs are intermittent
DG1 | DG2 | DG3 | R1 (s) | R2 (s) | R3 (s)
0 | 0 | 0 | 0.070 | N.O. | N.O.
0 | 0 | 1 | 0.071 | 0.100 | 0.304
0 | 1 | 0 | 0.071 | 0.100 | 0.304
0 | 1 | 1 | 0.071 | 0.112 | 0.312
1 | 0 | 0 | 0.070 | 0.100 | N.O.
1 | 0 | 1 | 0.070 | 0.100 | N.O.
1 | 1 | 0 | 0.071 | 0.112 | 0.304
1 | 1 | 1 | 0.071 | 0.112 | 0.312
Relay operating time for different DG configurations
0= disconnected, 1= connected, N.O.= No operation
In this analysis, DG connectivity changes with time
The same system is studied
Relay settings need to be changed depending on the system configuration
The protection is proposed with the aid of overcurrent relays and one way communication

## Slide 17: Conclusions
Current practice of DG disconnection for every fault in a network drastically reduces the DG benefits
Reliable protection solutions are needed to overcome these immediate DG disconnections
In this paper, protection strategies have been proposed to isolate the smallest portion of a faulted section without disconnecting DGs from the unfaulted sections
An overcurrent relay protection scheme has been proposed
If DGs are based on time varying sources, one way communication is used between DGs and relays
The proposed protection strategies help to maximize the DG benefits maintaining as many DG connections as possible